## Sheet1
负荷清单
Load List
序号 | 代号 | 名 称 | 名牌功率 | 数量 | Ps | Kx | COS¢ | tgφ | Pjs | Qjs | 标注
No. | Tag No. | Description | Rated Power | Quantity | [6 empty] | Remarks
上料系统 |  |  |  |  | 89.1
Feed System
1 | 0103 | 皮带秤 | 1.5 | 1 | 1.5 | 0.8 | 0.95 | 0.31 | 1.2 | 0.372 | 变频
|  | Belt Weigher | [8 empty] | VFD
2 | 0104 | 上料除尘器 | 6.6 | 1 | 6.6 | 0.7 | 0.8 | 0.75 | 4.62 | 3.465
Feed System Dust Collector
3 | 0104b | 除尘风机 | 22 | 1 | 22 | 0.8 | 0.8 | 0.75 | 17.6 | 13.2
Dust Collector Fan
4 | 0105 | 1#皮带机 | 11 | 1 | 11 | 0.7 | 0.8 | 0.75 | 7.7 | 5.775
Belt Conveyor No. 1
5 | 0106 | 板链式提升机 | 30 | 1 | 30 | 0.7 | 0.8 | 0.75 | 21 | 15.75
Plate Chain Bucket Elevator
6 | 0107 | 振动筛 | 5.5 | 1 | 5.5 | 0.8 | 0.8 | 0.75 | 4.4 | 3.3
Vibrating Screen
7 | 0109 | 散装机 | 1.5 | 1 | 1.5 | 0.7 | 0.8 | 0.75 | 1.05 | 0.7875
Bulk Loader
8 | 0110 | 2#皮带机 | 11 | 1 | 11 | 0.7 | 0.8 | 0.75 | 7.7 | 5.775
Belt Conveyor No. 2
预热系统 |  |  |  |  | 18.7
Preheating System
1 | 0201a | 1#油泵电机 | 18.5 | 1 | 18.5 | 0.8 | 0.8 | 0.75 | 14.8 | 11.1
Oil Pump Motor No. 1
2 | 0201b | 2#油泵电机 | 18.5 | 1 | 18.5 | 0 |  |  | 0 | 0 | 备用
|  | Oil Pump Motor No. 2 | [8 empty] | Standby
3 | 0201c | 加热器 | 5.5 | 1 | 5.5 | 0 |  |  | 0 | 0
Heater
4 | 0203 | 高温调节阀 | 0.1 | 2 | 0.2 | 0.5 | 0.8 | 0.75 | 0.1 | 0.075
High-Temperature Control Valve
回转窑系统 |  |  |  |  | 174.2
Rotary Kiln System
1 | 0301a | 主传动电机 | 160 | 1 | 160 | 0.8 | 0.95 | 0.31 | 128 | 39.68
Main Drive Motor
2 | 0301b | 主传冷却电机 | 2.2 | 1 | 2.2 | 0.8 | 0.8 | 0.75 | 1.76 | 1.32
Main Drive Cooling Motor
3 | 0301P | 减速机油泵 | 3 | 1 | 3 | 0.8 | 0.8 | 0.75 | 2.4 | 1.8
Gearbox Oil Pump
4 | 0301c | 窑辅传电机 | 15 | 1 | 15 | 0 |  |  | 0 | 0
Kiln Auxiliary Drive Motor
5 | 0301d | 挡轮油站 | 1.5 | 1 | 1.5 | 0.8 | 0.8 | 0.75 | 1.2 | 0.9
Thrust Roller Hydraulic Station
6 | 0302 | 窑头冷却风机 | 7.5 | 1 | 7.5 | 0.8 | 0.8 | 0.75 | 6 | 4.5
Kiln Hood Cooling Fan
3 | 0403 | 二次风机 | 110 | 1 | 110 | 0.8 | 0.95 | 0.31 | 88 | 27.28 | 变频
|  | Secondary Air Fan | [8 empty] | VFD
4 | 0403a | 二次风机冷却 | 1.1 | 1 | 1.1 | 0.7 | 0.8 | 0.75 | 0.77 | 0.5775
Secondary Air Fan Cooling
5 | 0403b | 电动风门 | 0.1 | 1 | 0.1 | 0.3 | 0.8 | 0.75 | 0.03 | 0.0225
Motorized Air Damper
6 | 0405 | 脉冲除尘器 | 7 | 1 | 7 | 0.7 | 0.8 | 0.75 | 4.9 | 3.675
Pulse-Jet Dust Collector
7 | 0406 | 离心风机 | 45 | 1 | 45 | 0.8 | 0.8 | 0.75 | 36 | 27
Centrifugal Fan
煅烧系统 |  |  |  |  | 57.05
Calcination System
1 | 0501 | 燃烧器 | 1.5 | 1 | 1.5 | 0.2 | 0.8 | 0.75 | 0.3 | 0.225
Burner
2 | 0502 | 一次风机 | 55 | 1 | 55 | 0.85 | 0.8 | 0.75 | 46.75 | 35.0625 | 变频
|  | Primary Air Fan | [8 empty] | VFD
3 | 0502a | 一次风机冷却 | 0.55 | 1 | 0.55 | 0.8 | 0.8 | 0.75 | 0.44 | 0.33
Primary Air Fan Cooling
成品输送系统 |  |  |  |  | 52.9
Finished Product Conveying System
1 | 0601 | 链斗输送机 | 11 | 1 | 11 | 0.8 | 0.8 | 0.75 | 8.8 | 6.6
Bucket Chain Conveyor
2 | 0602 | 斗提升机 | 30 | 1 | 30 | 0.8 | 0.8 | 0.75 | 24 | 18
Bucket Elevator
3 | 0602a | 辅助电机 | 7.5 | 1 | 7.5 | 0 | 0.8 | 0.75 | 0 | 0
Auxiliary Motor
4 | 0604 | 块状散装机 | 2.2 | 2 | 4.4 | 0.5 | 0.8 | 0.75 | 2.2 | 1.65
Lump Material Bulk Loader
废气处理系统 |  |  |  |  | 820.5
Exhaust Gas Treatment System
1 | 0701 | 袋式收尘器 | 1 | 1 | 1 | 0.7 | 0.8 | 0.75 | 0.7 | 0.525
Bag Filter
2 | 0702 | 冷风阀 | 0.25 | 1 | 0.25 | 0.3 | 0.8 | 0.75 | 0.075 | 0.05625
Cold Air Valve
3 | 0703 | 高温风机 | 710 | 1 | 710 | 0.8 | 0.95 | 0.31 | 568 | 176.08 | 10KV
High-Temperature Fan
4 | 0703a | 电动风门 | 0.35 | 1 | 0.35 | 0.3 | 0.8 | 0.75 | 0.105 | 0.07875
Motorized Air Damper
5 | 0705 | 气力输送 | 99.9 | 1 | 99.9 | 0.75 | 0.8 | 0.75 | 74.925 | 56.1938
Pneumatic Conveying System
6 | 0707 | 粉状散装机 | 1.5 | 1 | 1.5 | 0.5 | 0.8 | 0.75 | 0.75 | 0.5625
Powder Bulk Loader
7 | 0708 | 灰仓除尘器 | 7.5 | 1 | 7.5 | 0.7 | 0.8 | 0.75 | 5.25 | 3.9375
Product Silo Dust Collector
成品灰压球系统 |  |  |  |  | 407
Product Lime Briquetting System
1 | 0801 | 螺旋输送机 | 7.5 | 1 | 7.5 | 0.8 | 0.8 | 0.75 | 6 | 4.5 | 变频
|  | Screw Conveyor | [8 empty] | VFD
2 | 0802 | 刮板输送机 | 3 | 1 | 3 | 0.8 | 0.8 | 0.75 | 2.4 | 1.8
Scraper Conveyor
3 | 0803 | 电动三通阀 | 1.5 | 1 | 1.5 | 0.3 | 0.8 | 0.75 | 0.45 | 0.3375
Motorized Three-Way Valve
4 | 0804 | 斗式提升机 | 7.5 | 2 | 15 | 0.8 | 0.8 | 0.75 | 12 | 9
Bucket Elevator
5 | 0805 | 仓顶收尘器 | 3 | 2 | 6 | 0.7 | 0.8 | 0.75 | 4.2 | 3.15
Silo-Top Dust Collector
6 | 0806 | 螺旋输送机 | 3 | 2 | 6 | 0.8 | 0.95 | 0.31 | 4.8 | 1.488 | 变频
|  | Screw Conveyor | [8 empty] | VFD
7 | 0809 | 双轴搅拌机 | 11 | 2 | 22 | 0.8 | 0.8 | 0.75 | 17.6 | 13.2
Twin-Shaft Mixer
8 | 0810 | 压球机 | 170 | 2 | 340 | 0.7 | 0.8 | 0.75 | 238 | 178.5
Briquetting Press
9 | 0812 | 定量给料机 | 3 | 2 | 6 | 0.8 | 0.95 | 0.31 | 4.8 | 1.488
Weigh Feeder
∑Pjs | [8 empty] | 1371.775
Total Calculated Active Power (∑Pjs)
∑Qjs | [9 empty] | 679.1193
Total Calculated Reactive Power (∑Qjs)
Ps | 装机功率
Installed Power (Ps) | Installed Power
Kx | 需求系数
Demand Factor (Kx) | Demand Factor
cosφ | 功率因数
Power Factor (cosφ) | Power Factor
tgφ | 功率因数角正切值
Tangent of Power Factor Angle (tanφ) | Tangent of Power Factor Angle
Pjs | 计算有功功率
Calculated Active Power (Pjs) | Calculated Active Power
Qjs | 计算无功功率
Calculated Reactive Power (Qjs) | Calculated Reactive Power
∑Kp | 有功同时系数
Active-Power Coincidence Factor (∑Kp) | Active-Power Coincidence Factor
∑Kq | 无功同时系数
Reactive-Power Coincidence Factor (∑Kq) | Reactive-Power Coincidence Factor
∑Pjs | 总计算有功功率
Total Calculated Active Power (∑Pjs) | Total Calculated Active Power
∑Qjs | 总计算无功功率
Total Calculated Reactive Power (∑Qjs) | Total Calculated Reactive Power
Sjs | 总视在功率
Total Apparent Power (Sjs) | Total Apparent Power